## Sheet1
Name | Make | C | x | x**2 | y | y**2 | x*y | min x | max x | min y | max y
ReformEIRChiller McQuay WSC 471kW/5.89COP/Vanes CAPFT | McQuay | -0.48625 | -0.072932 | -0.0085148 | 0.14631 | -0.0044741 | 0.0098134 | 7.22 | 12.78 | 18.81 | 35.09
ReformEIRChiller McQuay WSC 816kW/6.74COP/Vanes CAPFT | McQuay | 0.92375 | 0.010133 | -0.0065643 | 0.027442 | -0.0021833 | 0.006538 | 7.22 | 12.78 | 19.41 | 33.45
ReformEIRChiller Carrier 19XR 869kW/5.57COP/VSD CAPFT | Carrier | 0.59899 | 0.10699 | -0.0084422 | -0.0016221 | -0.00043844 | 0.0023724 | 7.22 | 12.78 | 22.63 | 36.94
ReformEIRChiller Carrier 19XR 1143kW/6.57COP/VSD CAPFT | Carrier | 0.78639 | 0.032597 | -0.0019277 | 0.0043334 | -0.00060224 | 0.0018094 | 7.22 | 12.78 | 19.02 | 33.61
ReformEIRChiller Carrier 19XR 1234kW/5.39COP/VSD CAPFT | Carrier | 0.61343 | 0.10925 | -0.0073527 | -0.00259 | -0.00037935 | 0.00184 | 7.22 | 12.78 | 22.24 | 36.28
ReformEIRChiller Carrier 19XR 1259kW/6.26COP/Vanes CAPFT | Carrier | 1.0134 | -0.0031624 | -0.0044189 | 0.016011 | -0.0010297 | 0.0035089 | 7.22 | 12.78 | 22.61 | 36.74
ReformEIRChiller York YK 1259kW/6.45COP/Vanes CAPFT | York | 0.79177 | 0.077181 | -0.0018681 | 0.021684 | -0.0009454 | -0.00012515 | 7.22 | 12.78 | 19.63 | 32.83
ReformEIRChiller McQuay WSC 1519kW/7.10COP/Vanes CAPFT | McQuay | 1.2449 | -0.039883 | -0.0082939 | 0.030537 | -0.0028995 | 0.0097842 | 7.22 | 12.78 | 19.71 | 33.53
ReformEIRChiller Carrier 19XR 1586kW/5.53COP/VSD CAPFT | Carrier | 1.1322 | 0.0008236 | -0.00082076 | 0.0029677 | -0.00038983 | 0.0010158 | 7.22 | 12.78 | 23.36 | 36.72
ReformEIRChiller Carrier 19XR 1635kW/6.36COP/Vanes CAPFT | Carrier | 0.30929 | -0.032935 | -0.0047829 | 0.068602 | -0.0020176 | 0.0046707 | 7.22 | 12.78 | 20.44 | 36.54
ReformEIRChiller McQuay WSC 1751kW/6.73COP/Vanes CAPFT | McQuay | 0.69972 | 0.1013 | -0.0050696 | 0.015121 | -0.00091986 | 0.0011348 | 7.22 | 12.78 | 19.25 | 32.66
ReformEIRChiller York YK 1881kW/6.53COP/Vanes CAPFT | York | 0.80317 | 0.036187 | -0.0010275 | 0.012371 | -0.00074698 | 0.0011231 | 7.22 | 12.78 | 15 | 32.45
ReformEIRChiller York YK 1881kW/6.53COP/Vanes CAPFT_2 | York | 0.80317 | 0.036187 | -0.0010275 | 0.012371 | -0.00074698 | 0.0011231 | 7.22 | 12.78 | 15 | 32.45
ReformEIRChiller McQuay WDC 1973kW/6.28COP/Vanes CAPFT | McQuay | 1.3274 | 0.055891 | -0.0064184 | -0.028278 | -0.00026556 | 0.0029966 | 7.22 | 12.78 | 19.36 | 32.81
ReformEIRChiller York YK 1997kW/7.24COP/Vanes CAPFT | York | 1.0395 | 0.1593 | -0.0039891 | -0.038122 | 0.00028818 | -0.00075201 | 7.22 | 12.78 | 19.16 | 32.7
ReformEIRChiller McQuay PEH 1104kW/8.00COP/Vanes CAPFT | McQuay | 0.77578 | 0.017237 | -0.0027618 | 0.015602 | -0.0011332 | 0.0030427 | 6.67 | 12.22 | 22.59 | 34.29
ReformEIRChiller Carrier 19XR 1196kW/6.50COP/Vanes CAPFT | Carrier | 1.0066 | -0.035962 | -0.0025493 | 0.026903 | -0.0012551 | 0.0036699 | 6.67 | 12.22 | 21.72 | 33.03
ReformEIRChiller Carrier 19XR 1403kW/7.09COP/VSD CAPFT | Carrier | 0.85737 | -0.03077 | -0.0021713 | 0.022963 | -0.0010677 | 0.0031252 | 6.67 | 12.22 | 21.77 | 33.09
ReformEIRChiller Carrier 19XL 1797kW/5.69COP/Vanes CAPFT | Carrier | 0.91732 | 0.0499 | -0.001196 | -0.0020244 | -3.1417e-05 | -0.00037525 | 6.67 | 10 | 26.59 | 34.91
ReformEIRChiller Carrier 19XR 1801kW/6.34COP/VSD CAPFT | Carrier | 0.32773 | -0.094235 | -0.0017142 | 0.074968 | -0.0019875 | 0.0048074 | 6.67 | 12.22 | 19.63 | 32.95
ReformEIRChiller Carrier 19XR 2391kW/6.77COP/Vanes CAPFT | Carrier | -0.10923 | -0.07215 | -0.0019294 | 0.1074 | -0.0025859 | 0.0041634 | 6.67 | 12.22 | 19.72 | 32.63
ReformEIRChiller Carrier 19XR 2391kW/6.44COP/VSD CAPFT | Carrier | -0.11058 | -0.072157 | -0.0019244 | 0.10731 | -0.0025785 | 0.0041538 | 6.67 | 12.22 | 19.76 | 32.68
ReformEIRChiller McQuay PFH 4020kW/7.35COP/Vanes CAPFT | McQuay | 0.78402 | -0.020306 | -0.0060241 | 0.034645 | -0.0020158 | 0.0058763 | 6.67 | 12.22 | 23.88 | 34.13
ReformEIRChiller Carrier 23XL 1062kW/5.50COP/Valve CAPFT | Carrier | 1.0545 | 0.010157 | -0.004899 | -0.0037927 | -0.00036999 | 0.0028913 | 6.67 | 10 | 26.44 | 35.1
ReformEIRChiller Carrier 23XL 1196kW/6.39COP/Valve CAPFT | Carrier | 0.30314 | 0.0066679 | -0.003704 | 0.052468 | -0.0014089 | 0.0027756 | 6.67 | 12.22 | 20.39 | 32.63
ReformEIRChiller York YT 563kW/10.61COP/Vanes CAPFT | York | -0.28418 | -0.10063 | -0.0031576 | 0.12218 | -0.0030035 | 0.006704 | 6.11 | 12.78 | 18.47 | 33.52
ReformEIRChiller McQuay PEH 1030kW/8.58COP/Vanes CAPFT | McQuay | 0.63677 | 0.026379 | -0.004504 | 0.026146 | -0.0015096 | 0.0038093 | 6.11 | 12.78 | 20.86 | 32.69
ReformEIRChiller Trane CVHE 1329kW/5.38COP/Vanes CAPFT | Trane | 0.29713 | 0.10631 | -0.0044499 | 0.025404 | -0.00056962 | 0.00012699 | 6.11 | 10 | 26.77 | 41.98
ReformEIRChiller York YT 1125kW/7.92COP/VSD CAPFT | York | -0.18259 | -0.018907 | -0.0014525 | 0.094941 | -0.0021606 | 0.0028331 | 6.11 | 12.78 | 18.64 | 31.75
ReformEIRChiller York YT 1125kW/7.92COP/VSD CAPFT_2 | York | -0.18259 | -0.018907 | -0.0014525 | 0.094941 | -0.0021606 | 0.0028331 | 6.11 | 12.78 | 18.64 | 31.75
ReformEIRChiller Carrier 19XR 1213kW/7.78COP/Vanes CAPFT | Carrier | 0.75783 | -0.024675 | -0.0011852 | 0.030955 | -0.0011601 | 0.0023302 | 6.11 | 12.78 | 19.63 | 30.97
ReformEIRChiller Carrier 19XR 1294kW/7.61COP/Vanes CAPFT | Carrier | 0.85421 | -0.0054597 | -0.001943 | 0.016708 | -0.00090795 | 0.0023324 | 6.11 | 12.78 | 20.18 | 31.56
ReformEIRChiller Carrier 19XR 1410kW/8.54COP/VSD CAPFT | Carrier | 0.90538 | -0.01615 | -0.0011753 | 0.013181 | -0.00059192 | 0.0017568 | 6.11 | 12.78 | 19.05 | 30.63
ReformEIRChiller Carrier 19XR 1656kW/8.24COP/VSD CAPFT | Carrier | 0.36533 | -0.061392 | -0.0028159 | 0.07447 | -0.0024882 | 0.0050495 | 6.11 | 12.78 | 18.63 | 31.21
ReformEIRChiller Carrier 19XR 1723kW/8.32COP/VSD CAPFT | Carrier | 0.1239 | -0.071239 | -0.0026439 | 0.093965 | -0.0026437 | 0.0049239 | 6.11 | 12.78 | 18.07 | 31.4
ReformEIRChiller Carrier 19XR 1776kW/8.00COP/Vanes CAPFT | Carrier | -0.12212 | -0.061199 | -0.0017984 | 0.11626 | -0.0031624 | 0.0040888 | 6.11 | 12.78 | 18.69 | 30.73
ReformEIRChiller McQuay PFH 2043kW/8.44COP/Vanes CAPFT | McQuay | 0.75654 | 0.016907 | -0.0039883 | 0.020086 | -0.0014394 | 0.0039313 | 6.11 | 12.78 | 20.8 | 32.72
ReformEIRChiller York YS 672kW/7.90COP/Valve CAPFT | York | 0.9653 | 0.031179 | 0.00047478 | -0.0057784 | -1.2292e-05 | -0.00023487 | 6.11 | 12.78 | 23.07 | 32.6
ReformEIRChiller York YS 1171kW/9.15COP/Valve CAPFT | York | 0.93373 | 0.019206 | -0.00061156 | -0.00077719 | -0.00024831 | 0.00078725 | 6.11 | 12.78 | 21.56 | 30.78
ReformEIRChiller Trane CVHG670-44&86 2490kW/6.5COP CAPFT | Trane | 0.4036 | -0.0067942 | -0.00056495 | 0.046105 | -0.0011784 | 0.0021506 | 5.6 | 7.2 | 30.8 | 36.9
ReformEIRChiller McQuay PEH 703kW/7.03COP/Vanes CAPFT | McQuay | -0.13362 | 0.064732 | -0.012404 | 0.094256 | -0.0029589 | 0.0057655 | 5.56 | 8.89 | 20.28 | 31.25
ReformEIRChiller Carrier 23XL 724kW/6.04COP/Vanes CAPFT | Carrier | -0.1116 | -0.10584 | -0.0018297 | 0.096779 | -0.0021692 | 0.0049987 | 5.56 | 10 | 22.12 | 35.4
ReformEIRChiller Carrier 19XR 742kW/5.42COP/VSD CAPFT | Carrier | 0.77694 | -0.021497 | -0.0010801 | 0.027543 | -0.00079389 | 0.0016664 | 5.56 | 10 | 22.11 | 34.9
ReformEIRChiller Carrier 19XR 823kW/6.28COP/Vanes CAPFT | Carrier | 0.37466 | 0.085563 | -0.0030209 | 0.037454 | -0.0009995 | -4.4776e-05 | 5.56 | 10 | 17.99 | 29.36
ReformEIRChiller Carrier 19XR 897kW/7.23COP/VSD CAPFT | Carrier | 0.5212 | 0.079687 | -0.0014884 | 0.019748 | -0.00046435 | -0.00077867 | 5.56 | 10 | 18.72 | 30.41
ReformEIRChiller Carrier 19XR 897kW/6.50COP/Vanes CAPFT | Carrier | 0.5762 | 0.0058972 | -0.0008764 | 0.032073 | -0.0012252 | 0.0020198 | 5.56 | 10 | 18.06 | 29.67
ReformEIRChiller York YT 897kW/7.60COP/VSD CAPFT | York | 0.35482 | 0.0038018 | -0.0020811 | 0.055498 | -0.0022389 | 0.0037232 | 5.56 | 10 | 17.28 | 28.76
ReformEIRChiller York YT 897kW/6.27COP/VSD CAPFT | York | -0.12792 | 0.16536 | -0.0042025 | 0.048075 | -0.00095535 | -0.0021467 | 5.56 | 10 | 17.59 | 29.04
ReformEIRChiller Carrier 19XR 897kW/6.23COP/VSD CAPFT | Carrier | 0.8691 | 0.028858 | 0.00017954 | 0.0048687 | -0.00032079 | 0.0003825 | 5.56 | 10 | 18.61 | 30.29
ReformEIRChiller Carrier 19XR 1076kW/5.52COP/Vanes CAPFT | Carrier | 0.88505 | 0.028371 | -0.0055114 | 0.0081946 | -0.00066039 | 0.0029562 | 5.56 | 10 | 19.5 | 32.15
ReformEIRChiller York YT 1090kW/7.57COP/VSD CAPFT | York | 0.54328 | 0.048549 | -0.00087787 | 0.028144 | -0.00093141 | 0.00082406 | 5.56 | 10 | 19 | 30.79
ReformEIRChiller Trane CGWD 207kW/3.99COP/None CAPFT | Trane | 0.95855 | 0.035169 | 0.00012466 | -0.0027456 | -5.0002e-05 | -0.00017235 | 5.56 | 10 | 29.37 | 40.94
ReformEIRChiller Carrier 19XR 1157kW/5.62COP/VSD CAPFT | Carrier | 1.0955 | -0.0055461 | -0.00051866 | 0.0014204 | -0.00028016 | 0.0010079 | 5.56 | 10 | 21.97 | 34.5
ReformEIRChiller McQuay PEH 1231kW/6.18COP/Vanes CAPFT | McQuay | 1.2534 | 0.088751 | -0.0083234 | -0.010245 | -0.00067513 | 0.0024561 | 5.56 | 8.89 | 20.98 | 31.25
ReformEIRChiller York YT 1266kW/4.39COP/Vanes CAPFT | York | 0.0015565 | -0.044109 | -0.0018545 | 0.064116 | -0.0012047 | 0.0030604 | 5.56 | 8.89 | 17.28 | 42.31
ReformEIRChiller Carrier 19XR 1284kW/6.20COP/Vanes CAPFT | Carrier | 1.1158 | -0.029639 | -0.0011357 | 0.0041841 | -0.00043829 | 0.0020965 | 5.56 | 8.89 | 19.55 | 30.85
ReformEIRChiller Carrier 19XR 1350kW/7.90COP/VSD CAPFT | Carrier | 1.0606 | -0.028172 | -0.0010795 | 0.0039771 | -0.00041661 | 0.0019928 | 5.56 | 8.89 | 19.55 | 30.85
ReformEIRChiller McQuay PFH 1407kW/6.60COP/Vanes CAPFT | McQuay | 0.48575 | -0.11393 | -0.010362 | 0.11463 | -0.0045476 | 0.012631 | 5.56 | 8.89 | 21.9 | 32.26
ReformEIRChiller Trane CVHE 1125kW/4.89COP/Vanes CAPFT | Trane | 0.37387 | -0.019664 | -0.0012121 | 0.035495 | -0.00058 | 0.0012505 | 5.56 | 10 | 26.1 | 36.56
ReformEIRChiller York YT 1495kW/7.51COP/VSD CAPFT | York | 0.60155 | -0.16301 | 0.0099519 | 0.074529 | -0.0016082 | 0.0020019 | 5.56 | 8.89 | 18.69 | 41.38
ReformEIRChiller Carrier 19XR 1558kW/5.81COP/VSD CAPFT | Carrier | 1.0629 | 0.017954 | -0.0013933 | -0.00096698 | -0.00025801 | 0.00077348 | 5.56 | 10 | 20.93 | 32.69
ReformEIRChiller York YT 1663kW/9.34COP/Vanes CAPFT | York | 0.69727 | -0.096923 | 0.0048467 | 0.055235 | -0.0019953 | 0.0035334 | 5.56 | 8.89 | 18.45 | 34.43
ReformEIRChiller Trane CVHF 2184kW/6.78COP/Vanes CAPFT | Trane | 1.2145 | -0.014957 | -0.0029342 | 0.015689 | -0.00097802 | 0.0027233 | 5.56 | 10 | 30.67 | 36.06
ReformEIRChiller York YT 1758kW/5.76COP/VSD CAPFT | York | 0.19608 | 0.14628 | -0.0045681 | 0.031853 | -0.00062901 | -0.0012795 | 5.56 | 10.51 | 21.27 | 32.81
ReformEIRChiller York YT 1758kW/6.26COP/Vanes CAPFT | York | 0.48419 | -0.024372 | 0.0032445 | 0.055904 | -0.0013028 | 0.00092571 | 5.56 | 10 | 21.48 | 33.76
ReformEIRChiller York YT 1758kW/5.96COP/Vanes CAPFT | York | 0.80757 | 0.052879 | -0.00044938 | 0.0070361 | -0.00035368 | 0.00037314 | 5.56 | 10 | 21.29 | 33.53
ReformEIRChiller Carrier 19XR 1758kW/5.86COP/VSD CAPFT | Carrier | 0.095283 | -0.041191 | -0.0038543 | 0.076985 | -0.001945 | 0.0042851 | 5.56 | 10 | 17.86 | 31.43
ReformEIRChiller York YT 1794kW/8.11COP/Vanes CAPFT | York | 1.4756 | -0.248 | 0.013534 | 0.052163 | -0.0023301 | 0.0051319 | 5.56 | 8.89 | 18.71 | 34.34
ReformEIRChiller York YT 1794kW/7.90COP/VSD CAPFT | York | 0.74318 | -0.17388 | 0.007863 | 0.067807 | -0.001637 | 0.0034096 | 5.56 | 8.89 | 17.43 | 35.71
ReformEIRChiller York YT 1934kW/7.55COP/Vanes CAPFT | York | -0.80345 | 0.056209 | -0.0010663 | 0.13777 | -0.0031234 | 0.0010427 | 5.56 | 8.89 | 19.55 | 35.11
ReformEIRChiller McQuay PEH 1934kW/6.01COP/Vanes CAPFT | McQuay | -0.40439 | -0.056953 | -0.0013535 | 0.12156 | -0.002814 | 0.0041618 | 5.56 | 8.89 | 19 | 36.6
ReformEIRChiller Trane RTHB 531kW/4.83COP/Valve CAPFT | Trane | 0.908 | 0.011472 | 0.00084742 | 0.0077508 | -0.00029553 | 0.00036206 | 5.56 | 10 | 25.39 | 34.83
ReformEIRChiller York YT 2110kW/7.15COP/Vanes CAPFT | York | 0.061326 | -0.011422 | 0.0016604 | 0.083454 | -0.0021591 | 0.0016998 | 5.56 | 8.89 | 18.99 | 34.89
ReformEIRChiller McQuay PFH 2124kW/6.03COP/Vanes CAPFT | McQuay | 0.84667 | -0.038096 | 0.00040039 | 0.029137 | -0.001138 | 0.0024053 | 5.56 | 8.89 | 20.28 | 36.13
ReformEIRChiller Trane RTHB 542kW/5.26COP/Valve CAPFT | Trane | 0.92924 | 0.029772 | 0.00042797 | -0.00018256 | -9.1435e-05 | -8.4718e-05 | 5.56 | 10 | 25.39 | 34.83
ReformEIRChiller York YT 2233kW/9.54COP/VSD CAPFT | York | 0.44156 | -0.085656 | 0.0059915 | 0.072541 | -0.0021 | 0.0022353 | 5.56 | 8.89 | 17.85 | 34.04
ReformEIRChiller York YT 2233kW/9.54COP/VSD CAPFT_2 | York | 0.49396 | -0.097438 | 0.0067828 | 0.071492 | -0.0020775 | 0.0022466 | 5.56 | 8.89 | 17.93 | 34.11
ReformEIRChiller McQuay PFH 2462kW/6.67COP/Vanes CAPFT | McQuay | 0.41423 | 0.015426 | -0.007911 | 0.075084 | -0.0027737 | 0.0058374 | 5.56 | 8.89 | 21.31 | 31.55
ReformEIRChiller Trane CVHF 1779kW/6.18COP/Vanes CAPFT | Trane | -0.13797 | -0.088173 | -0.0015512 | 0.092976 | -0.001943 | 0.0040505 | 5.56 | 10 | 27.96 | 34.47
ReformEIRChiller Trane CVHF 1681kW/6.59COP/Vanes CAPFT | Trane | 0.68493 | -0.097459 | -0.0065165 | 0.04596 | -0.0015969 | 0.0071027 | 5.56 | 10 | 27.96 | 34.43
ReformEIRChiller York YT 3133kW/9.16COP/Vanes CAPFT | York | 0.61122 | -0.014307 | 9.8237e-05 | 0.032935 | -0.0012219 | 0.0026593 | 5.56 | 8.89 | 19.37 | 35.91
ReformEIRChiller McQuay PFH 3165kW/6.48COP/Vanes CAPFT | McQuay | 1.5758 | 0.033401 | -0.012946 | -0.021362 | -0.0010763 | 0.0072873 | 5.56 | 8.89 | 20.9 | 31.43
ReformEIRChiller Trane RTHC 1066kW/5.73COP/Valve CAPFT | Trane | 1.132 | 0.053503 | 0.00046741 | -0.0096968 | -1.0926e-05 | -0.00068641 | 5.56 | 10 | 27.08 | 33
ReformEIRChiller Trane CVHF 1758kW/6.87COP/Vanes CAPFT | Trane | 0.79501 | 0.031706 | -0.00055476 | 0.0042685 | -0.0001289 | 0.00045091 | 5.56 | 10 | 20.44 | 32.98
ReformEIRChiller Trane RTHB 538kW/5.12COP/Valve CAPFT | Trane | 0.93268 | 0.027456 | 0.00039911 | 0.0010739 | -0.00013356 | 1.3999e-05 | 5.56 | 10 | 23.52 | 32.74
ReformEIRChiller Trane CVHF 1758kW/5.96COP/Vanes CAPFT | Trane | 1.1529 | -0.00399 | -0.0031887 | -0.017133 | 0.00010136 | 0.00238 | 5.56 | 10 | 20.13 | 32.4
ReformEIRChiller Trane CVHF 1758kW/6.46COP/VSD CAPFT | Trane | 1.1555 | -0.0060173 | -0.0030521 | -0.016152 | 0.00011787 | 0.0022136 | 5.56 | 10 | 20.1 | 32.22
ReformEIRChiller Carrier 23XL 686kW/5.91COP/Valve CAPFT | Carrier | 0.012489 | -0.038907 | -0.0044826 | 0.086328 | -0.0022893 | 0.0047555 | 5.56 | 10 | 17.39 | 30.39
ReformEIRChiller York YS 756kW/7.41COP/Valve CAPFT | York | 0.96429 | 0.028664 | 0.00031091 | -0.0056313 | -3.7626e-05 | -5.2372e-05 | 5.56 | 10 | 20.05 | 28.28
ReformEIRChiller Carrier 23XL 830kW/6.97COP/Valve CAPFT | Carrier | 0.75938 | 0.0031282 | -0.00024618 | 0.016485 | -0.00033427 | 0.00024981 | 5.56 | 10 | 18.74 | 28.78
ReformEIRChiller Carrier 23XL 862kW/6.11COP/Valve CAPFT | Carrier | -0.29791 | -0.051512 | -0.0033838 | 0.11082 | -0.0025697 | 0.0038037 | 5.56 | 10 | 16.41 | 29.48
ReformEIRChiller Carrier 23XL 862kW/6.84COP/Valve CAPFT | Carrier | -0.3093 | -0.052866 | -0.0033257 | 0.11244 | -0.002612 | 0.0038254 | 5.56 | 10 | 16.41 | 29.48
ReformEIRChiller Trane RTHC 1009kW/5.37COP/Valve CAPFT | Trane | 1.2076 | 0.036346 | 0.00063315 | -0.01094 | -4.3763e-05 | -0.00027638 | 5.56 | 10 | 26.58 | 31.91
ReformEIRChiller Trane RTHC 1094kW/6.55COP/Valve CAPFT | Trane | 0.99371 | 0.041212 | 0.00056471 | -0.0044667 | -6.2552e-05 | -0.00029594 | 5.56 | 10 | 22.5 | 31.57
ReformEIRChiller Trane CVHE 1129kW/7.19COP/Vanes CAPFT | Trane | 0.042349 | -0.067114 | -0.0026778 | 0.085348 | -0.0022409 | 0.0050285 | 5.56 | 10 | 20.75 | 30.64
ReformEIRChiller Trane RTHC 707kW/7.77COP/Valve CAPFT | Trane | 0.96508 | 0.031165 | 0.00062832 | -0.0051587 | -5.982e-05 | -0.00016233 | 5.56 | 11.11 | 21.4 | 30.31
ReformEIRChiller Carrier 23XL 1108kW/6.92COP/Valve CAPFT | Carrier | 0.51583 | -0.023116 | -0.00070133 | 0.041069 | -0.0011773 | 0.0022925 | 5.56 | 10 | 18.28 | 30.24
ReformEIRChiller York YS 1554kW/9.31COP/Valve CAPFT | York | 1.1583 | 0.0098113 | 0.0012271 | -0.015354 | 9.923e-05 | 5.3237e-05 | 5.56 | 8.89 | 20.74 | 40.06
ReformEIRChiller Trane CVHE 1080kW/7.39COP/Vanes CAPFT | Trane | 0.16216 | -0.056378 | -0.0027636 | 0.076584 | -0.0021675 | 0.0049402 | 5.56 | 10 | 20.34 | 28.77
ReformEIRChiller McQuay PEH 819kW/8.11COP/Vanes CAPFT | McQuay | 0.55191 | 0.013933 | -0.0048181 | 0.037057 | -0.0014298 | 0.003474 | 4.44 | 8.89 | 18.51 | 35.07
ReformEIRChiller York YT 1023kW/5.81COP/Vanes CAPFT | York | -0.33958 | -0.030843 | -0.0055206 | 0.11121 | -0.002663 | 0.0050999 | 4.44 | 8.89 | 18.34 | 40.55
ReformEIRChiller York YT 1048kW/6.06COP/Vanes CAPFT | York | 0.58467 | 0.010599 | -0.0050587 | 0.030061 | -0.00093644 | 0.0025972 | 4.44 | 8.89 | 20.43 | 39.72
ReformEIRChiller York YT 1055kW/5.96COP/Vanes CAPFT | York | -0.27075 | -0.069046 | -0.0028622 | 0.11167 | -0.002741 | 0.0055738 | 4.44 | 8.89 | 17.24 | 39.89
ReformEIRChiller Trane CVHE 1442kW/6.61COP/VSD CAPFT | Trane | -0.26607 | -0.02115 | -0.00039285 | 0.095739 | -0.0020159 | 0.00203 | 4.44 | 8.89 | 19.72 | 41.41
ReformEIRChiller Trane RTWA 383kW/4.17COP/Valve CAPFT | Trane | 1.005 | 0.038968 | 9.2704e-05 | -0.0043468 | -4.9616e-05 | -0.00024014 | 4.44 | 8.89 | 29.19 | 40.69
ReformEIRChiller York YT 1368kW/7.35COP/VSD CAPFT | York | -0.19889 | -0.1019 | -0.0046056 | 0.13642 | -0.0041428 | 0.008791 | 4.44 | 8.89 | 17.76 | 34.51
ReformEIRChiller Trane RTHB 1051kW/5.05COP/Valve CAPFT | Trane | 0.96382 | 0.03356 | -6.6978e-05 | -0.0031428 | -6.684e-05 | 1.8417e-05 | 4.44 | 8.89 | 28.94 | 40.58
ReformEIRChiller York YT 1396kW/7.35COP/Vanes CAPFT | York | 0.036013 | -0.097711 | -0.0028452 | 0.11245 | -0.0034777 | 0.0076886 | 4.44 | 8.89 | 17.94 | 34.67
ReformEIRChiller York YT 1403kW/6.94COP/VSD CAPFT | York | -1.7217 | 0.085943 | -0.012208 | 0.20374 | -0.0046547 | 0.0047013 | 4.44 | 8.89 | 21.33 | 36.28
ReformEIRChiller Trane CVHE 1758kW/5.96COP/Vanes CAPFT | Trane | -0.37842 | -0.083332 | -0.0085097 | 0.10319 | -0.0024323 | 0.0070655 | 4.44 | 8.89 | 28.68 | 40.15
ReformEIRChiller Carrier 19XR 1407kW/6.04COP/VSD CAPFT | Carrier | 0.90065 | -0.011397 | -0.0014806 | 0.027709 | -0.00096172 | 0.001813 | 4.44 | 10 | 18.11 | 37.42
ReformEIRChiller York YT 1459kW/6.40COP/VSD CAPFT | York | -1.194 | 0.24664 | -0.017708 | 0.12032 | -0.0025701 | 0.00084972 | 4.44 | 8.89 | 21.15 | 37.17
ReformEIRChiller McQuay PEH 1635kW/7.47COP/Vanes CAPFT | McQuay | 0.83078 | -0.021694 | -0.0031846 | 0.029458 | -0.0014128 | 0.003406 | 4.44 | 8.89 | 19.47 | 34.79
ReformEIRChiller Carrier 19XL 1674kW/7.89COP/Vanes CAPFT | Carrier | -0.16047 | -0.05171 | -0.0015025 | 0.10782 | -0.0024025 | 0.0030632 | 4.44 | 8.89 | 17.74 | 34.74
ReformEIRChiller Carrier 19XR 1727kW/9.04COP/Vanes CAPFT | Carrier | 0.25747 | 0.0022726 | -0.0058156 | 0.065402 | -0.0019588 | 0.0037011 | 4.44 | 8.89 | 18.94 | 35.13
ReformEIRChiller Trane CVHE 1484kW/9.96COP/VSD CAPFT | Trane | -0.97591 | -0.14469 | -0.0046943 | 0.1963 | -0.0045438 | 0.0089981 | 4.44 | 8.89 | 17.08 | 35.97
ReformEIRChiller Trane CVHF 2317kW/6.33COP/VSD CAPFT | Trane | 0.66325 | 0.0046086 | -0.0011001 | 0.016516 | -0.00047537 | 0.0016483 | 4.44 | 8.89 | 17.67 | 35.67
ReformEIRChiller York YT 1758kW/6.28COP/Vanes CAPFT | York | 0.50626 | -0.0093739 | -0.0028228 | 0.042022 | -0.0010921 | 0.0020745 | 4.44 | 8.89 | 20.46 | 39.72
ReformEIRChiller Trane CVHF 2567kW/11.77COP/VSD CAPFT | Trane | 0.31507 | 0.0076687 | -0.0043485 | 0.049989 | -0.0012421 | 0.0031583 | 4.44 | 8.89 | 17.02 | 35.24
ReformEIRChiller Trane CVHF 2799kW/6.40COP/Vanes CAPFT | Trane | -0.21763 | -0.049413 | 8.7006e-05 | 0.096121 | -0.0020276 | 0.0025388 | 4.44 | 8.89 | 20.38 | 35.07
ReformEIRChiller Carrier 19XL 1779kW/6.18COP/Vanes CAPFT | Carrier | -0.074219 | -0.068646 | -0.0066568 | 0.097786 | -0.0026802 | 0.0067656 | 4.44 | 8.89 | 20.83 | 32.12
ReformEIRChiller Trane CVHF 2043kW/9.08COP/Vanes CAPFT | Trane | -2.2153 | -0.032946 | -0.0053007 | 0.23416 | -0.0045587 | 0.0046312 | 4.44 | 8.89 | 23.06 | 34.9
ReformEIRChiller York YT 1867kW/10.09COP/Vanes CAPFT | York | -0.086218 | -0.042828 | -0.0044674 | 0.0989 | -0.0027681 | 0.0057282 | 4.44 | 8.89 | 17.96 | 39.35
ReformEIRChiller Carrier 19XL 1871kW/6.49COP/Vanes CAPFT | Carrier | -0.7422 | -0.058932 | -0.0063598 | 0.1451 | -0.0034168 | 0.0059058 | 4.44 | 8.89 | 20.92 | 35.06
ReformEIRChiller York YT 1881kW/6.77COP/VSD CAPFT | York | 0.25108 | -0.039977 | -0.0036279 | 0.068195 | -0.0021353 | 0.0052451 | 4.44 | 8.89 | 17.8 | 35.02
ReformEIRChiller McQuay PEH 1895kW/6.42COP/Vanes CAPFT | McQuay | 0.45184 | -0.15356 | 0.0017602 | 0.081231 | -0.0024605 | 0.0063719 | 4.44 | 8.89 | 17.93 | 40.14
ReformEIRChiller Carrier 19XL 2057kW/6.05COP/Vanes CAPFT | Carrier | 0.64481 | -0.03315 | -0.0031685 | 0.031965 | -0.0011389 | 0.0037997 | 4.44 | 8.89 | 17.89 | 35.37
ReformEIRChiller York YK 2159kW/6.85COP/Vanes CAPFT | York | -0.051641 | -0.073849 | -0.010362 | 0.12014 | -0.0038811 | 0.009873 | 4.44 | 8.89 | 21.13 | 34.75
ReformEIRChiller York YK 2201kW/6.69COP/Vanes CAPFT | York | -0.21327 | -0.097123 | -0.0074453 | 0.13334 | -0.0039713 | 0.0092479 | 4.44 | 8.89 | 21.11 | 34.92
ReformEIRChiller York YK 2237kW/6.41COP/Vanes CAPFT | York | 0.26863 | -0.040511 | -0.0021302 | 0.076746 | -0.0022825 | 0.0044783 | 4.44 | 8.89 | 21.3 | 35.03
ReformEIRChiller York YK 2275kW/6.32COP/Vanes CAPFT | York | 0.39429 | -0.05577 | -0.0011056 | 0.069014 | -0.0020901 | 0.0043923 | 4.44 | 8.89 | 21.39 | 35.17
ReformEIRChiller York YK 2275kW/6.32COP/Vanes CAPFT_2 | York | 0.92274 | -0.033819 | 0.00044029 | 0.025283 | -0.0011312 | 0.0028445 | 4.44 | 8.89 | 18.78 | 35.17
ReformEIRChiller Trane CVHF 2300kW/8.10COP/Vanes CAPFT | Trane | 0.04946 | 0.017632 | -0.0017079 | 0.080244 | -0.0023015 | 0.0023344 | 4.44 | 8.89 | 19.58 | 34.79
ReformEIRChiller Trane CVHF 4610kW/6.34COP/Vanes CAPFT | Trane | 0.80542 | -0.010863 | -0.0017507 | 0.012693 | -0.00039133 | 0.0016021 | 4.44 | 8.89 | 23.15 | 34.76
ReformEIRChiller York YK 2412kW/5.58COP/Vanes CAPFT | York | 0.60422 | -0.0052828 | -0.00019937 | 0.029723 | -0.0008288 | 0.0015879 | 4.44 | 8.89 | 21.3 | 35.78
ReformEIRChiller York YK 2771kW/6.84COP/VSD CAPFT | York | 0.47442 | 0.031781 | -0.0018028 | 0.053809 | -0.0016427 | 0.0013304 | 4.44 | 8.89 | 18.24 | 34.26
ReformEIRChiller Trane CVHE 1407kW/7.14COP/VSD CAPFT | Trane | 0.10986 | -0.041548 | -0.006348 | 0.088016 | -0.0026314 | 0.0058461 | 4.44 | 8.89 | 17.66 | 34.28
ReformEIRChiller York YK 4396kW/6.63COP/Vanes CAPFT | York | -0.79351 | -0.18597 | -0.011362 | 0.22236 | -0.0069107 | 0.016081 | 4.44 | 7.78 | 18.53 | 31.58
ReformEIRChiller York YK 4477kW/6.64COP/Vanes CAPFT | York | -0.56126 | -0.20941 | -0.0085555 | 0.20507 | -0.0064515 | 0.015611 | 4.44 | 7.78 | 18.5 | 31.67
ReformEIRChiller York YK 4515kW/6.22COP/Vanes CAPFT | York | 0.20751 | -0.01981 | -0.0028927 | 0.05882 | -0.0015216 | 0.0034612 | 4.44 | 7.78 | 17.15 | 31.76
ReformEIRChiller York YK 4537kW/6.28COP/Vanes CAPFT | York | 0.17693 | 0.00080334 | -0.012996 | 0.11602 | -0.0041927 | 0.0093398 | 4.44 | 7.78 | 19.77 | 31.78
ReformEIRChiller Trane CVHE 1372kW/7.49COP/Vanes CAPFT | Trane | 0.33976 | 0.034316 | -0.010088 | 0.057665 | -0.0023007 | 0.0060355 | 4.44 | 8.89 | 17.87 | 34.26
ReformEIRChiller Carrier 19EX 4667kW/6.16COP/Vanes CAPFT | Carrier | -0.089157 | -0.064913 | -0.0033567 | 0.11085 | -0.0030343 | 0.0056481 | 4.44 | 7.78 | 17.77 | 31.94
ReformEIRChiller York YK 4966kW/6.05COP/Vanes CAPFT | York | 0.4673 | -0.038811 | -0.00024626 | 0.036055 | -0.00080101 | 0.0021909 | 4.44 | 8.89 | 20.07 | 35.01
ReformEIRChiller York YK 4969kW/7.14COP/Vanes CAPFT | York | 0.0028116 | -0.17889 | -0.0046406 | 0.1472 | -0.0046252 | 0.011084 | 4.44 | 8.89 | 18.57 | 34.55
ReformEIRChiller York YK 4969kW/7.07COP/Vanes CAPFT | York | -1.2384 | -0.21671 | -0.0095258 | 0.24815 | -0.0069303 | 0.01496 | 4.44 | 8.89 | 21.3 | 34.56
ReformEIRChiller Carrier 19EX 4997kW/6.40COP/Vanes CAPFT | Carrier | -0.26861 | -0.046402 | -0.0077911 | 0.11161 | -0.0030408 | 0.0068233 | 4.44 | 7.78 | 17.18 | 32.28
ReformEIRChiller Carrier 19EX 5148kW/6.34COP/Vanes CAPFT | Carrier | -0.10112 | -0.010846 | -0.0068044 | 0.088698 | -0.0023435 | 0.004797 | 4.44 | 8.89 | 20.87 | 34.96
ReformEIRChiller York YK 5170kW/7.15COP/Vanes CAPFT | York | -1.064 | -0.22332 | -0.0074412 | 0.22819 | -0.0062689 | 0.01391 | 4.44 | 8.89 | 21.3 | 34.88
ReformEIRChiller Carrier 19EX 5208kW/6.88COP/Vanes CAPFT | Carrier | 0.12545 | -0.10282 | -0.0042428 | 0.09373 | -0.0027338 | 0.0071614 | 4.44 | 8.89 | 21.08 | 35.31
ReformEIRChiller York YK 5465kW/6.94COP/Vanes CAPFT | York | -1.005 | -0.20208 | -0.0057681 | 0.2097 | -0.005538 | 0.011959 | 4.44 | 8.89 | 21.03 | 34.99
ReformEIRChiller York YK 5549kW/6.50COP/Vanes CAPFT | York | -0.862 | 0.0066928 | -0.0040202 | 0.15501 | -0.003587 | 0.0030271 | 4.44 | 8.89 | 18.38 | 31.7
ReformEIRChiller Carrier 19FA 5651kW/5.50COP/Vanes CAPFT | Carrier | 0.92051 | -0.078308 | -0.0045451 | 0.058531 | -0.0021087 | 0.0063593 | 4.44 | 8.89 | 26.23 | 39.12
ReformEIRChiller Multistack MS 172kW/3.67COP/None CAPFT | Unknown | 1.1273 | 0.12218 | -0.0047461 | -0.02834 | 0.00030215 | -0.00066165 | 4.44 | 8.89 | 23.82 | 40.51
ReformEIRChiller Trane CVHF 4677kW/6.27COP/Vanes CAPFT | Trane | 0.81383 | -0.023159 | 0.0061811 | 0.0086396 | -0.00018072 | -5.0159e-05 | 4.44 | 7.78 | 17.51 | 31.94
ReformEIRChiller York YS 781kW/5.42COP/Valve CAPFT | York | 1.0334 | 0.035158 | 0.00042883 | -0.0057374 | -2.6471e-05 | -0.00022229 | 4.44 | 8.89 | 21.31 | 41.08
ReformEIRChiller York YS 1758kW/5.84COP/Valve CAPFT | York | 0.63485 | -0.025238 | -0.00184 | 0.038304 | -0.00099619 | 0.0019066 | 4.44 | 8.89 | 17.74 | 39.72
ReformEIRChiller McQuay PFH 932kW/5.09COP/Vanes CAPFT | McQuay | 1.0212 | -0.0016802 | -0.0052231 | 0.029222 | -0.0014189 | 0.0042113 | 3.33 | 7.78 | 19.66 | 35.59
ReformEIRChiller York YT 960kW/4.64COP/Vanes CAPFT | York | -0.34746 | 0.40715 | -0.032707 | 0.011873 | -0.00031179 | 0.00058547 | 3.33 | 7.78 | 17.04 | 35.78
ReformEIRChiller Carrier 23XL 865kW/6.05COP/Valve CAPFT | Carrier | 0.40949 | -0.026037 | -0.0031922 | 0.03485 | -0.00065723 | 0.0021946 | 3.33 | 7.78 | 16.5 | 35.26
ReformEIRChiller York YS 879kW/5.82COP/Valve CAPFT | York | 1.0431 | 0.032073 | -0.00033726 | -0.0018027 | -0.00017302 | 0.0003613 | 3.33 | 7.78 | 18.15 | 35.12

## Sheet2
CWRT (F) | ReformEIRChiller Trane CGWD 207kW/3.99COP/None CAPFT | ReformEIRChiller Trane CVHF 2184kW/6.78COP/Vanes CAPFT | ReformEIRChiller Trane CVHF 2043kW/9.08COP/Vanes CAPFT | ReformEIRChiller Trane CVHF 1758kW/6.87COP/Vanes CAPFT | ReformEIRChiller Trane CVHE 1407kW/7.14COP/VSD CAPFT | ReformEIRChiller Trane CVHF 2567kW/11.77COP/VSD CAPFT | ReformEIRChiller Trane CVHF 1681kW/6.59COP/Vanes CAPFT | ReformEIRChiller Trane CVHE 1442kW/6.61COP/VSD CAPFT | ReformEIRChiller Trane CVHF 2317kW/6.33COP/VSD CAPFT | ReformEIRChiller Trane RTHB 1051kW/5.05COP/Valve CAPFT | ReformEIRChiller Trane RTHB 542kW/5.26COP/Valve CAPFT | ReformEIRChiller Trane RTHB 538kW/5.12COP/Valve CAPFT | ReformEIRChiller Trane CVHF 4610kW/6.34COP/Vanes CAPFT | ReformEIRChiller Trane CVHE 1080kW/7.39COP/Vanes CAPFT | ReformEIRChiller Trane RTHC 1094kW/6.55COP/Valve CAPFT | ReformEIRChiller Trane RTHB 531kW/4.83COP/Valve CAPFT | ReformEIRChiller Trane CVHF 1779kW/6.18COP/Vanes CAPFT | ReformEIRChiller Trane CVHF 1758kW/5.96COP/Vanes CAPFT | ReformEIRChiller Trane CVHE 1372kW/7.49COP/Vanes CAPFT | ReformEIRChiller Trane RTHC 1066kW/5.73COP/Valve CAPFT | ReformEIRChiller Trane RTHC 1009kW/5.37COP/Valve CAPFT | ReformEIRChiller Trane CVHF 4677kW/6.27COP/Vanes CAPFT | ReformEIRChiller Trane CVHF 1758kW/6.46COP/VSD CAPFT | ReformEIRChiller Trane CVHF 2300kW/8.10COP/Vanes CAPFT | ReformEIRChiller Trane CVHE 1125kW/4.89COP/Vanes CAPFT | ReformEIRChiller Trane RTWA 383kW/4.17COP/Valve CAPFT | ReformEIRChiller Trane CVHG670-44&86 2490kW/6.5COP CAPFT | ReformEIRChiller Trane CVHE 1758kW/5.96COP/Vanes CAPFT | ReformEIRChiller Trane CVHE 1329kW/5.38COP/Vanes CAPFT | ReformEIRChiller Trane RTHC 707kW/7.77COP/Valve CAPFT | ReformEIRChiller Trane CVHE 1484kW/9.96COP/VSD CAPFT | ReformEIRChiller Trane CVHE 1129kW/7.19COP/Vanes CAPFT | ReformEIRChiller Trane CVHF 2799kW/6.40COP/Vanes CAPFT
65 |  |  |  |  | 1.008 | 1.044 |  |  | 0.966 | [9 empty] | 1.118 |  |  | 0.968 | [8 empty] | 1.063
66 |  |  |  |  | 1.02 | 1.056 |  |  | 0.97 | [9 empty] | 1.121 |  |  | 0.969 | [8 empty] | 1.106
67 |  |  |  |  | 1.031 | 1.067 |  |  | 0.974 | [9 empty] | 1.122 |  |  | 0.97 | [8 empty] | 1.146
68 |  |  |  |  | 1.04 | 1.077 |  | 0.938 | 0.978 | [9 empty] | 1.123 |  |  | 0.971 |  | 1.038 | [6 empty] | 1.184
69 |  |  |  | 1.039 | 1.048 | 1.087 |  | 0.952 | 0.982 |  |  |  |  | 0.986 |  |  |  | 0.995 | 1.122 |  |  | 0.971 | 0.998 | 1.038 | [6 empty] | 1.218 |  | 0.92
70 |  |  |  | 1.04 | 1.054 | 1.096 |  | 0.965 | 0.985 |  |  |  |  | 0.994 |  |  |  | 0.995 | 1.119 |  |  | 0.972 | 0.999 | 1.037 | [6 empty] | 1.25 | 0.98 | 0.934
71 |  |  |  | 1.04 | 1.059 | 1.104 |  | 0.977 | 0.988 |  |  |  |  | 1 |  |  |  | 0.995 | 1.115 |  |  | 0.972 | 1 | 1.034 | [5 empty] | 0.998 | 1.279 | 0.989 | 0.947
72 |  |  |  | 1.041 | 1.061 | 1.111 |  | 0.987 | 0.991 |  |  |  |  | 1.005 |  |  |  | 0.995 | 1.109 |  |  | 0.972 | 1 | 1.03 | [5 empty] | 0.993 | 1.305 | 0.998 | 0.959
73 |  |  |  | 1.041 | 1.062 | 1.117 |  | 0.996 | 0.993 |  |  |  |  | 1.009 | 1.068 |  |  | 0.996 | 1.103 |  |  | 0.973 | 1.001 | 1.024 | [5 empty] | 0.989 | 1.328 | 1.005 | 0.969
74 |  |  | 1.02 | 1.042 | 1.062 | 1.123 |  | 1.004 | 0.995 |  |  |  | 0.982 | 1.011 | 1.063 |  |  | 0.996 | 1.094 |  |  | 0.973 | 1.002 | 1.017 | [5 empty] | 0.984 | 1.348 | 1.01 | 0.979
75 |  |  | 1.045 | 1.042 | 1.06 | 1.128 |  | 1.01 | 0.997 |  |  | 1.049 | 0.984 | 1.012 | 1.058 |  |  | 0.997 | 1.085 |  |  | 0.973 | 1.003 | 1.008 | [5 empty] | 0.979 | 1.366 | 1.014 | 0.987
76 |  |  | 1.067 | 1.043 | 1.056 | 1.132 |  | 1.016 | 0.998 |  |  | 1.046 | 0.985 | 1.011 | 1.053 |  |  | 0.997 | 1.074 |  |  | 0.972 | 1.004 | 0.998 | [5 empty] | 0.974 | 1.381 | 1.017 | 0.993
77 |  |  | 1.086 | 1.043 | 1.051 | 1.136 |  | 1.02 | 1 |  |  | 1.043 | 0.986 | 1.01 | 1.048 |  |  | 0.998 | 1.061 |  |  | 0.972 | 1.005 | 0.987 | [5 empty] | 0.969 | 1.393 | 1.018 | 0.999
78 |  |  | 1.102 | 1.043 | 1.044 | 1.138 |  | 1.023 | 1.001 |  | 1.031 | 1.04 | 0.987 | 1.007 | 1.043 | 1.054 |  | 0.999 | 1.047 |  |  | 0.972 | 1.006 | 0.974 | [5 empty] | 0.964 | 1.402 | 1.018 | 1.003
79 |  |  | 1.116 | 1.043 | 1.035 | 1.14 |  | 1.024 | 1.001 |  | 1.028 | 1.037 | 0.988 | 1.002 | 1.038 | 1.051 |  | 0.999 | 1.032 |  |  | 0.971 | 1.008 | 0.959 | 0.94 |  |  |  |  | 0.959 | 1.408 | 1.017 | 1.006
80 |  |  | 1.127 | 1.043 | 1.025 | 1.141 |  | 1.025 | 1.001 |  | 1.025 | 1.033 | 0.989 | 0.996 | 1.033 | 1.048 |  | 1 | 1.015 |  | 1.065 | 0.97 | 1.009 | 0.944 | 0.947 |  |  |  |  | 0.953 | 1.412 | 1.014 | 1.008
81 |  |  | 1.135 | 1.043 | 1.013 | 1.141 |  | 1.024 | 1.002 |  | 1.022 | 1.03 | 0.989 | 0.989 | 1.027 | 1.045 |  | 1.001 | 0.997 | 1.068 | 1.057 | 0.97 | 1.01 | 0.927 | 0.953 |  |  |  | 1.039 | 0.948 | 1.413 | 1.01 | 1.009
82 |  |  | 1.14 | 1.043 | 1 | 1.141 |  | 1.021 | 1.001 |  | 1.019 | 1.026 | 0.989 | 0.981 | 1.022 | 1.041 |  | 1.002 | 0.977 | 1.06 | 1.049 | 0.969 | 1.012 | 0.908 | 0.959 |  |  |  | 1.036 | 0.943 | 1.411 | 1.005 | 1.008
83 |  |  | 1.142 | 1.042 | 0.985 | 1.14 | 1.081 | 1.018 | 1.001 |  | 1.016 | 1.023 | 0.989 | 0.971 | 1.017 | 1.037 | 1.036 | 1.003 | 0.956 | 1.052 | 1.04 | 0.968 | 1.013 | 0.888 | 0.964 |  |  |  | 1.033 | 0.938 | 1.406 | 0.998 | 1.006
84 |  |  | 1.141 | 1.042 | 0.968 | 1.138 | 1.077 | 1.013 | 1 |  | 1.013 | 1.019 | 0.988 |  | 1.011 | 1.033 | 1.039 | 1.004 | 0.934 | 1.044 | 1.032 | 0.967 | 1.015 | 0.867 | 0.969 |  |  | 0.981 | 1.029 | 0.933 | 1.398 | 0.989 | 1.003
85 | 1.005 |  | 1.138 | 1.042 | 0.95 | 1.135 | 1.073 | 1.008 | 0.999 | 1.001 | 1.009 | 1.016 | 0.988 |  | 1.006 | 1.029 | 1.04 | 1.005 | 0.91 | 1.036 | 1.024 | 0.965 | 1.017 | 0.844 | 0.974 | 1.014 |  | 0.982 | 1.025 | 0.927 | 1.388 | 0.98 | 0.998
86 | 1.002 |  | 1.132 | 1.041 | 0.93 | 1.132 | 1.068 | 1 | 0.997 | 0.997 | 1.006 | 1.012 | 0.987 |  | 1 | 1.025 | 1.04 | 1.006 | 0.884 | 1.029 | 1.015 | 0.964 | 1.018 | 0.82 | 0.978 | 1.009 |  | 0.98 | 1.021 | 0.922 | 1.375 | 0.969 | 0.992
87 | 0.998 |  | 1.123 | 1.041 | 0.908 | 1.127 | 1.062 | 0.992 | 0.996 | 0.993 | 1.003 | 1.008 | 0.985 |  | 0.995 | 1.02 | 1.039 | 1.007 | 0.858 | 1.021 | 1.007 | 0.963 | 1.02 | 0.794 | 0.983 | 1.004 |  | 0.978 | 1.016 |  | 1.359 | 0.956 | 0.985
88 | 0.994 | 1.053 | 1.111 | 1.04 | 0.885 | 1.122 | 1.054 | 0.982 | 0.994 | 0.989 | 0.999 | 1.004 | 0.984 |  | 0.989 | 1.016 | 1.036 | 1.009 | 0.829 | 1.013 | 0.999 | 0.961 | 1.022 | 0.767 | 0.986 | 1 | 1.014 | 0.973 | 1.011 |  | 1.34 |  | 0.977
89 | 0.99 | 1.036 | 1.097 | 1.039 | 0.86 | 1.117 | 1.046 | 0.972 | 0.991 | 0.985 | 0.995 | 1 | 0.982 |  |  | 1.011 | 1.033 | 1.01 | 0.8 | 1.005 | 0.99 | 0.959 | 1.024 | 0.739 | 0.99 | 0.995 | 1.005 | 0.968 | 1.006 |  | 1.318 |  | 0.968
90 | 0.987 | 1.018 | 1.079 | 1.038 | 0.834 | 1.11 | 1.037 | 0.96 | 0.989 | 0.981 | 0.992 | 0.996 | 0.981 |  |  | 1.006 | 1.028 | 1.012 | 0.769 | 0.997 |  |  |  | 0.709 | 0.993 | 0.99 | 0.996 | 0.961 | 1 |  | 1.294 |  | 0.957
91 | 0.983 | 1 | 1.059 | 1.038 | 0.806 | 1.103 | 1.027 | 0.946 | 0.986 | 0.977 | 0.988 |  | 0.978 |  |  | 1 | 1.022 |  | 0.736 | 0.989 |  |  |  | 0.677 | 0.995 | 0.985 | 0.985 | 0.952 | 0.994 |  | 1.266 |  | 0.945
92 | 0.979 | 0.981 | 1.036 |  | 0.776 | 1.095 | 1.015 | 0.932 | 0.982 | 0.973 | 0.984 |  | 0.976 |  |  | 0.995 | 1.015 |  | 0.703 |  |  |  |  | 0.645 | 0.997 | 0.98 | 0.974 | 0.942 | 0.988 |  | 1.236 |  | 0.932
93 | 0.975 | 0.962 | 1.01 |  | 0.744 | 1.086 | 1.003 | 0.916 | 0.979 | 0.968 | 0.981 |  | 0.973 |  |  | 0.989 | 1.006 |  | 0.667 |  |  |  |  | 0.61 | 0.999 | 0.975 | 0.962 | 0.93 | 0.981 |  | 1.204 |  | 0.917
94 | 0.971 | 0.942 | 0.981 |  |  | 1.076 |  | 0.899 | 0.975 | 0.964 | 0.977 |  | 0.971 |  |  | 0.984 | 0.997 | [6 empty] | 0.575 | 1.001 | 0.97 | 0.95 | 0.917 | 0.974 |  | 1.168 |  | 0.902
95 | 0.967 | 0.921 |  |  |  | 1.066 |  | 0.88 | 0.971 | 0.96 | [14 empty] | 1.002 | 0.965 | 0.937 | 0.902 | 0.966 |  | 1.129 |  | 0.885
96 | 0.963 | 0.9 | [5 empty] | 0.861 | 0.967 | 0.956 | [14 empty] | 1.003 | 0.96 | 0.923 | 0.886 | 0.959 |  | 1.088
97 | 0.959 | [6 empty] | 0.84 |  | 0.951 | [14 empty] | 1.004 | 0.955 | 0.908 | 0.868 | 0.95
98 | 0.955 | [6 empty] | 0.818 |  | 0.947 | [15 empty] | 0.949 | 0.893 | 0.849 | 0.942
99 | 0.951 | [6 empty] | 0.795 |  | 0.942 | [15 empty] | 0.944 |  | 0.828 | 0.933
100 | 0.947 | [6 empty] | 0.77 |  | 0.938 | [15 empty] | 0.939 |  | 0.806 | 0.924

## Sheet3
0.10986 | 5.55 | 20 | 1.0404
-0.041548
-0.006348
0.088016
-0.0026314
0.0058461